## Read me
Commissioning issue log
The Definitive Guide to AI Data Centers — aidatacenterguide.com · v1.0 · defaults as of 2026-07
Intended user | Commissioning agent (CxA) and the owner's project team, from L1 factory witness through L5 IST and the first 90 days of operations.
What it is | The single controlled register of every discrepancy found during commissioning: one row per issue, with level, system, severity, root cause, resolution, retest evidence, and two-party sign-off. An issue is closed only when the CxA and the owner's representative both sign.
Required inputs / units | Dates ISO (YYYY-MM-DD). Level = Cx level where found (L1 factory … L5 integrated systems test, OPS for post-handover). Severity A = safety / blocks energization or IST; B = blocks turnover of the system; C = must fix before first ramp; D = punch-list.
Reference design | Worked rows show a liquid-cooled AI build (CDU, UPS, EPMS examples). Delete them and start at the next ID.
Canonical chapters | Ch 13.1 (program governance), Ch 13.2 (documentation & acceptance scripts), Ch 13.6 (Level 5 IST) — aidatacenterguide.com/part-13-commissioning-and-go-live
Document control
Project
Document no.
Revision
Date
Prepared by
Reviewed by (discipline)
Approved by (owner)
This template is a starting frame, not engineering. Project-specific values require review and approval by the responsible engineer of record / authority named above.

## Issue log
Issue log
One row per issue. Shaded rows are a worked example — delete before use.
ID | Date found | Level | System | Location | Description of discrepancy | Severity | Safety flag | Responsible party | Root cause | Corrective action / resolution | Retest date | Retest evidence (doc ref) | Status | CxA sign-off / date | Owner sign-off / date
CX-0001 | 2026-05-14 | L3 | Electrical — UPS A | Elec room 1A | UPS module 3 transferred to static bypass at 62% step load during L3 load-bank test; spec requires ride-through to 100%. | B | No | UPS vendor FSE | DSP firmware at N-1 revision; transfer threshold mis-set | Firmware updated to R7.2; transfer threshold reset per submittal; step-load retest 0→100% passed. | 2026-05-21 | LB-UPS-A-r2.pdf | Closed | JMR 2026-05-21 | KTW 2026-05-22
CX-0002 | 2026-06-02 | L4 | Mechanical — CDU 07 | Data hall 2, row G | CDU 07 secondary-loop flow 12% below design at 100% pump speed; ΔP across strainer 2.1× commissioning baseline. | C | No | Mech GC | Construction debris in Y-strainer; flushing plan skipped final velocity pass | Loop re-flushed to spec velocity; strainer cleaned; flow verified at design ±3%; flushing NCR raised against MC. | 2026-06-05 | CDU07-flow-r1.xlsx | Closed | JMR 2026-06-05 | KTW 2026-06-06
CX-0003 | 2026-06-18 | L5 | EPMS / controls | Site-wide | During utility-loss IST scenario 4, EPMS load-shed stage 2 tripped non-critical mechanical loads 8 s late; generators held. | B | No | Controls integrator | Shed-stage timer inherited default from library template | Timer corrected; scenario 4 re-run witnessed; all stages within spec. |  |  | Open — retest scheduled

## Legend
Levels & severity
L1 | Factory acceptance / witness testing (FAT)
L2 | Site acceptance of delivered equipment (SAT)
L3 | Pre-functional / component start-up and verification
L4 | Functional performance testing, system by system
L5 | Integrated systems testing (IST) — whole-building failure-mode demonstration
OPS | Found after handover, within the warranty/seasonal-test window
Severity A | Safety hazard or blocks energization/IST — stop-work until resolved
Severity B | Blocks turnover or acceptance of the affected system
Severity C | Must close before first production ramp
Severity D | Punch-list; close by warranty walkdown