## Read me
FMEA / FMECA starter — AI data center
The Definitive Guide to AI Data Centers — aidatacenterguide.com · v1.0 · defaults as of 2026-07
Intended user | Reliability engineer / owner's engineer building the site failure-mode register — typically at 60–90% design, revisited before IST and after any major retrofit.
What it is | A failure-modes-and-effects starter sheet with the standard S×O×D risk-priority scoring. RPN is computed by formula; the ratings legend pins the 1–10 anchors so scores are comparable across reviewers.
Required inputs / units | S (severity), O (occurrence), D (detection) each 1–10 per the Ratings sheet. RPN = S×O×D; review every mode ≥ 120, and every mode with S ≥ 9 regardless of RPN.
Reference design | Worked rows cover a liquid-cooled AI hall (CDU pump, UPS module, cooling-controls sensor). They are illustrative anchors — delete and build the register from your single-line and P&IDs.
Canonical home | Appendix F — Failure-Mode / FMEA Catalog (aidatacenterguide.com); Ch 12.1 for fault-domain engineering.
Document control
Project
Document no.
Revision
Date
Prepared by
Reviewed by (discipline)
Approved by (owner)
This template is a starting frame, not engineering. Project-specific values require review and approval by the responsible engineer of record / authority named above.

## FMEA
FMEA register
Shaded rows are a worked example — delete before use. RPN column is a formula.
ID | System / item | Function | Failure mode | Local effect | System / mission effect | S | Potential cause | O | Detection / control | D | RPN | Mitigation / design change | Owner | Status
FM-001 | CDU 07 — secondary pump | Circulate coolant to 8 racks | Mechanical seal leak | Coolant loss into containment pan; pump degraded | Rack inlet temp rises; thermal throttling of ~1 MW of compute within minutes | 7 | Seal wear; water chemistry out of spec | 4 | Leak detection in pan; ΔP/flow monitoring; N+1 pump auto-start | 3 |  | Quarterly chemistry sampling; seal replacement at 3 yr; verify N+1 failover in seasonal test | Mech lead | Open
FM-002 | UPS system A — power module | Ride through utility events for hall A | DC-bus capacitor end-of-life failure | Module derates or trips offline | Redundancy loss (N during maintenance window); no load drop unless coincident fault | 8 | Capacitor aging beyond service interval | 3 | Impedance trending in EPMS; annual thermography | 4 |  | Capacitor replacement program per vendor life; alarm-on-trend before failure | Elec lead | Open
FM-003 | Cooling controls — supply-temp sensor (hall B header) | Feed CDU setpoint control | Sensor drift (reads low) | Controls raise supply temp above actual setpoint | Fleet-wide silent margin erosion; throttling during a hot-day peak | 6 | Uncalibrated sensor; no cross-check | 5 | Single sensor, no voting — weak until redundant sensing added | 7 |  | Add 2oo3 voting on hall supply headers; calibration in the seasonal-test scope | Controls | Open

## Ratings
Rating anchors (1–10)
Severity (S)
1–2 Cosmetic / no operational effect
3–4 Single-rack or single-system degradation, no SLA impact
5–6 Hall-level derate or throttling; recoverable without load loss
7–8 Load loss or redundancy exhausted in one fault domain
9–10 Safety hazard, or site-level outage / multi-domain load loss
Occurrence (O)
1–2 Not expected in site life (>20 yr MTBF class)
3–4 Possible once in 5–20 yr
5–6 Expected every 1–5 yr
7–8 Several times per year
9–10 Continuous / chronic exposure
Detection (D) — lower is better-detected
1–2 Automatic detection + automatic safe response, proven in IST
3–4 Automatic alarm with procedure-driven response
5–6 Detected on routine rounds / trending only
7–8 Detected only by failure symptoms
9–10 No credible detection before mission effect